## Slide 1
FM + COVID-19 Series #16
Strategies in Operational Performance and IAQ Improvements During and After COVID-19
IFMA.org

## Slide 2
Coronavirus Resource Center
ifma.org/coronavirus
IFMA.org

## Slide 3
Strategies in Operational Performance and IAQ Improvements During and After COVID-19
Dr. Ashish Mathur
Vice President of Innovation, UVDI
Dr. Marwa Zaatari
Chief Science Officer, Blue Box Air
Carlos Santamaria
CEES-Advisors, Principal
Moderator

## Slide 4
Today’s Topics
The important role HVAC plays during COVID-19
Basics of UVC disinfection
Cost effective strategies to optimize energy and IAQ
Operational awareness of HVAC systems
Open Discussion and Q & A

## Slide 5: HVAC Strategies in the Age of COVID
Marwa Zaatari, PhD
August 12, 2020

## Slide 6: Can HVAC System Design and Operation Prevent COVID-19 Airborne Transmission?
Increased OA for Ventilation
Flushing Sequence
Operate Ultraviolet Germicidal Irradiation
Operate Economizers
Continuous Run of toilet’s Exhaust system
Maintain normal thermal comfort conditions
Filtration (MERV 13 min)
Operate standalone air cleaners
HVAC Coil Cleaning using enzymes
Increase room air motion

## Slide 7: Recommendations by order of effectiveness, first and operating cost
1) Source Control
2) Source Removal
3) Dilution

## Slide 8: Trade-off Between Filtration and Ventilation
Wells Riley Risk infection Model
OA + PM Filtration | Risk (%) | Relative First Cost ($) | Relative Annual Cost ($)
Min OA + MERV 7 | 14.38% | $ - | $-
Min OA+ MERV 13 | 9.40% | $324 | $1,295
100 % OA | 8.51% | $906,275 | $189,751

## Slide 9: Coil Cleaning
“A substantial evidence exists that coils can disseminate contaminants into the indoor air. ”
Goals:
Remove biofilms deep within the coil
Not to re-aerosolize any particles that may be on the surface
 Traditional coil cleaning (pressure and steam washing) and UV does not establish the above.

## Slide 10: COVID-19 Testing
Air Sample Test
Swab Test
Pump

## Slide 11
X-rays
100
200
280
315
400
780
Wavelength (nm)
UV
UV
-C
UV-B
UV
-A
Ultraviolet
Visible Light
Infrared
Vacuum-
Cell Inactivation of Microorganisms
Electromagnetic Spectrum
Increasing Wavelength
Increasing Energy
260
What is Ultraviolet Light?

## Slide 12
Ultraviolet Germicidal Irradiation
The 254nm Energy Damages the DNA of the Pathogens
How UV Disinfects
UV-C energy alters the DNA of microorganisms preventing them from reproducing and causing them to become non-pathogenic, or incapable of causing disease.

## Slide 13: Correct Application of UVC Dose

## Slide 14
Cooling Coil Disinfection
Air Stream Disinfection
Surface Room Disinfection
UVC Applications in Buildings

## Slide 15: UVGI Air Stream Disinfection
“Kill on the Fly”
COMMON AIRBORNE MICROORGANISMS
CORONAVIRUS, INFLUENZA , SARS, HIN1, MERS-CoV
TUBERCULOSIS
MEASLES
ASPERGILLUS MOLD SPORES
LEGIONELLA

## Slide 16
Duct Mounted
AHU Mounted
UVGI Air Disinfection

## Slide 17
Air Stream Disinfection is HIGH intensity light
Fractions of a second to “kill” the microbe
  Traveling 500fpm with a “kill” zone of 2 feet is 0.24009 seconds
Air Stream Disinfection can clean a coil if next to the cooling coil
Key Takeaway – Air Disinfection
Dose = Intensity Time
x

## Slide 18: Coronavirus Preventative Measures
Greater than 99% single pass reduction of Coronavirus when Airstream disinfection sized for 90% single pass reduction of Influenza A

## Slide 19: UV Air Stream Disinfection Example Duct Installation

## Slide 20: UV Coil + Air Stream Disinfection Example AHU Installation

## Slide 21: UVGI Upper Air Room Disinfection
UVC Fixtures installed at a height above 7 ft
Baffles/louvers direct UVC outwards and upwards preventing occupant UVC exposure
Good room circulation allows UVC light to disinfect air as it moves upwards
Courtesy: Dr. Richard Vincent Mt. Sinai School of Medicine, NY

## Slide 22: UVGI Whole Room Surface Disinfection
Coronavirus droplets can travel and deposit on surfaces in a room
Studies indicate coronavirus and other pathogens can survive on surfaces for days and weeks
UVC proven to be very effective in disinfecting surfaces to high levels of disinfection

## Slide 23
Audience Q & A
Notes: Is the vision to go back to pre-COVID?

## Slide 24
Wednesday, August 19th
10:00 A.M. CDT
FM + COVID-19 Series #17
How technology and automation can improve O & M in your critical facilities
https://covid-19webinar.ifma.org

## Slide 25
Coronavirus Resource Center
ifma.org/coronavirus
IFMA.org